## Summary
Project |  | Reserve at Gum Springs ; Century Communities | [11 empty] | Date: |  | 2017-09-20
Location |  | Jefferson, GA | [11 empty] | By: |  | WHM
Description |  | Guava - A2/B2, Slab, Bed 5, Bed 6, Optional Covered Patio | [11 empty] | House Faces: |  |  | Worst | South
BUILDING DATA | [5 empty] | DESIGN CONDITIONS | [8 empty] | ENERGY CALCULATIONS
Typical Ceiling Height |  |  | 9 | ft |  |  |  | Summer |  | Winter
Floor Area |  |  | 3014 | ft2 |  | Outdoor |  | 95 | °Fdb | 18 | °Fdb
Volume |  |  | 25564 | ft3 |  | Indoor |  | 75 | °Fdb | 72 | °Fdb
Building Tightness |  |  | Tight | 0.25 |  | Delta T |  | 20 | °Fdb | 54 | °Fdb
[6 empty] | Range |  | 17.3 | °Fdb
Construction Descriptions
Walls / Partitions | # | U-Value | Description / Notes
| W1 | 0.077 | Above Grade |  |  |  |  | 2x4 |  |  |  | R-13 batt
| W2 | 0.067 | Basement |  |  |  |  | Concrete + 2x4 |  |  |  | R-13 batt
| W3 | 0.077 | Attic |  |  |  |  | 2x6 |  |  |  | R19 batt
Doors | # | U-Value | Description / Notes
| D1 | 0.5 | Exterior Door | [8 empty] | R-2
| D2 | 0.5 | Garage Door | [8 empty] | R-2
Roofs | # | U-Value | Description / Notes
| R1 | 0.026 | Flat Ceiling |  |  |  |  | Truss |  |  |  | R-38 Blown
| R2 | 0.053 | Vaulted |  |  |  |  | Truss |  |  |  | R-30 Batt
Floors | # | U-Value | Description / Notes
| F1 | 0.053 | Framed |  |  |  |  | I-Joist |  |  |  | R-19 batt
| F2 | 0.1 | Slab | [8 empty] | None
Glass | # | Glass Type |  |  |  |  | Windows |  |  | U-Value |  | Internal Shading |  |  |  |  | Notes
| G1 | Double Insulated |  |  |  |  | All Types |  |  | 0.32 |  | Blinds/ Draperies |  |  |  |  | SHGC | 0.22
G2
G3
Load Summary
[5 empty] | Unit 1 |  |  | Unit 2 |  |  |  |  | Unit 3
[5 empty] | Cooling | Heating |  | Cooling |  | Heating |  |  | Cooling |  |  | Heating
Sensible Load |  |  |  | btu/hr | 29363.2795 | 35132.937 |  | 0 |  | 0
Minimum Nominal Capacity |  |  |  | tons | 3.2626 | 10.2939 | kW | 0 |  | 0 | kW
Load Density |  |  |  | sf/ton | 923.8069 | 3.4153 | W/sf
Floor Area Served |  |  |  | sf | 3014
System Size |  |  |  | tons | 4 | 10 | kW
Leaving Air Temperature |  |  |  | °f | 57.2 | 96.3
Installed Capacity |  |  |  | sf/ton | 753.5 | 3.3179 | w/sf

## Rooms Walls and Glass
Room Name |  |  | Foyer & Hall | Garage Entry | Pantry | Kitchen | Dining | Great Room | Bath 4 | Bed 6 | Stairs | Hallway | Bath 3 | Bed 4 | Bed 4 WIC | Bed 5 | Bed 3 | Bed 3 WIC | Bed 2 & WIC | Bath 2 | Owner WIC | Owner Bath | Owner Suite | Laundry
Front Faces: | East |  | Unit 1 a | Unit 1 a | Unit 1 a | Unit 1 a | Unit 1 a | Unit 1 a | Unit 1 a | Unit 1 a | Unit 1 b | Unit 1 b | Unit 1 b | Unit 1 b | Unit 1 b | Unit 1 b | Unit 1 b | Unit 1 b | Unit 1 b | Unit 1 b | Unit 1 b | Unit 1 b | Unit 1 b | Unit 1 b
People | [7 empty] | 1 |  | 1 |  |  |  | 1 |  | 1 | 1 |  | 1 |  |  |  | 1
Appliances | [5 empty] | 680 |  | 250 | [15 empty] | 200
Glass & Doors |  |  | Glass & Doors
Direction | Facing | Type | Foyer & Hall | Garage Entry | Pantry | Kitchen | Dining | Great Room | Bath 4 | Bed 6 | Stairs | Hallway | Bath 3 | Bed 4 | Bed 4 WIC | Bed 5 | Bed 3 | Bed 3 WIC | Bed 2 & WIC | Bath 2 | Owner WIC | Owner Bath | Owner Suite | Laundry | 0 | 0 | 0
North | Right | G1 | [6 empty] | 8 |  | 15
Northeast |  | G1
East | Front | G1 | [11 empty] | 30 |  | 15 | 15
SouthEast |  | G1
South | Left | G1 | [16 empty] | 15
SouthWest |  | G1
West | Back | G1 |  |  |  | 16 | 40 | 45 | [14 empty] | 45
NorthWest |  | G1
Sky Light |  | G1
Shaded |  | G1 | 10 | [6 empty] | 36
Door 1 |  | D1 | 10
Door 2 |  | D2 |  | 17.8
Above Grade Walls |  |  | Above Grade Walls
Direction | Facing | Type | Foyer & Hall | Garage Entry | Pantry | Kitchen | Dining | Great Room | Bath 4 | Bed 6 | Stairs | Hallway | Bath 3 | Bed 4 | Bed 4 WIC | Bed 5 | Bed 3 | Bed 3 WIC | Bed 2 & WIC | Bath 2 | Owner WIC | Owner Bath | Owner Suite | Laundry | 0 | 0 | 0
North | Right | W1 | [5 empty] | 181 | 55 | 145 | 123 |  | 74 | 113 | [8 empty] | 163
Northeast |  | W1
East | Front | W1 | 40 | [6 empty] | 97 |  |  |  | 90 |  | 98 | 103
SouthEast |  | W1
South | Left | W1 |  |  | 46 | 181 |  |  |  | 22 |  |  |  | 20 |  |  | 119 | 43 | 96 |  | 123
SouthWest |  | W1
West | Back | W1 |  |  |  | 117 | 58 | 115 | [12 empty] | 96 | 104 | 106
NorthWest |  | W1
Exterior Perimeter |  |  | 5.5556 | 1.9778 | 5.1111 | 33.1111 | 6.4444 | 32.8889 | 6.1111 | 29.3333 | 13.6667 | - | 8.2222 | 24.7778 | - | 10.8889 | 24.6667 | 4.7778 | 10.6667 | - | 24.3333 | 11.5556 | 29.8889 | - | - | - | -
Basement Walls
Direction | Facing | Type | Foyer & Hall | Garage Entry | Pantry | Kitchen | Dining | Great Room | Bath 4 | Bed 6 | Stairs | Hallway | Bath 3 | Bed 4 | Bed 4 WIC | Bed 5 | Bed 3 | Bed 3 WIC | Bed 2 & WIC | Bath 2 | Owner WIC | Owner Bath | Owner Suite | Laundry | 0 | 0 | 0
North | Right | W1
Northeast |  | W1
East | Front | W1
SouthEast |  | W1
South | Left | W1
SouthWest |  | W1
West | Back | W1
NorthWest |  | W1
Exterior Perimeter |  |  | 1.1111 | 1.9778 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Other Walls | [27 empty] | O
Grade |  | W2
Partition |  | W1
Garage |  | W1 | 193 | 99 | 100
Attic |  | W3
Kneewall |  | W3 | [19 empty] | 29
Roofs & Floors | [27 empty] | O
Ceiling |  | R1 | [8 empty] | 74 | 155 | 46 | 174 | 22 | 177 | 177 | 29 | 183 | 63 | 145 | 138 | 282 | 68 |  |  |  |  | .
Vaulted |  | R2
Crawl/Uncon. |  | F1
Garage |  | F1 | [9 empty] | 55 |  |  |  | 90 | 177 | 29 | 37 | 9
Slab |  | F2 | 213 | 65 | 46 | 240 | 178 | 290 | 57 | 192 | 66

## Unit 1 a
Project |  |  | Reserve at Gum Springs ; Century Communities | [7 empty] | Date: | 2017-09-20 | [5 empty] | Typical Ceiling Height |  |  | 9
Location |  |  | Jefferson, GA | [7 empty] | By:
Description |  |  | Guava - A2/B2, Slab, Bed 5, Bed 6, Optional Covered Patio | [7 empty] | Level(s): | First Floor |  |  | Unit 1 a |  |  | Kneewall Height |  |  | 1
|  |  | Square Feet |  | 1281 | Volume | 11700 | Sf/Ton | 640.5 |  | SEER | 14
[7 empty] | Ceiling Height |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 12 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 8 |  | 8 |  | 8
Components |  |  | CLTD (°F) | U-Value (Btu/hr-sf-°F) | Cooling Load Factor |  | Entire House |  | Foyer & Hall |  | Garage Entry |  | Pantry |  | Kitchen |  | Dining |  | Great Room |  | Bath 4 |  | Bed 6
| Type | Description |  |  |  |  | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr
Glass | G1 | North | Right | (E) | 5.8773 | Btu/hr-sf | 8 | 47.0181 |  | - |  | - |  | - |  | - |  | - |  | - | 8 | 47.0181 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | Northeast |  | (SE) | 7.5027 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | East | Front | (S) | 12.63 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | SouthEast |  | (SW) | 13.9472 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | South | Left | (W) | 15.5451 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | SouthWest |  | (NW) | 25.896 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | West | Back | (N) | 28.8737 | Btu/hr-sf | 101 | 2916.2462 |  | - |  | - |  | - | 16 | 461.9796 | 40 | 1154.949 | 45 | 1299.3176 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | NorthWest |  | (NE) | 17.9826 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | Sky Light |  |  | 40 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | Shaded |  |  | 5.8773 | Btu/hr-sf | 46 | 270.3542 | 10 | 58.7727 |  | - |  | - |  | - |  | - |  | - |  | - | 36 | 211.5816 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Door | D1 | Door 1 | 21 | 0.5 | 10.5 | Btu/hr-sf | 10 | 105 | 10 | 105 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| D2 | Door 2 | 30 | 0.5 | 15 | Btu/hr-sf | 17.8 | 267 |  | - | 17.8 | 267 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Above Grade Walls | W1 | North | 13 | 0.077 | 1.001 | Btu/hr-sf | 381 | 381.381 |  | - |  | - |  | - |  | - |  | - | 181 | 181.181 | 55 | 55.055 | 145 | 145.145 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Northeast | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | East | 23 | 0.077 | 1.771 | Btu/hr-sf | 137 | 242.627 | 40 | 70.84 |  | - |  | - |  | - |  | - |  | - |  | - | 97 | 171.787 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthEast | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | South | 16 | 0.077 | 1.232 | Btu/hr-sf | 249 | 306.768 |  | - |  | - | 46 | 56.672 | 181 | 222.992 |  | - |  | - |  | - | 22 | 27.104 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthWest | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | West | 23 | 0.077 | 1.771 | Btu/hr-sf | 290 | 513.59 |  | - |  | - |  | - | 117 | 207.207 | 58 | 102.718 | 115 | 203.665 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | NorthWest | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Basement Walls | W1 | North | 13 | 0.077 | 1.001 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Northeast | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | East | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthEast | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | South | 16 | 0.077 | 1.232 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthWest | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | West | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | NorthWest | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Other | W2 | Grade | 0 | 0.067 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Partition | 10 | 0.077 | 0.77 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Garage | 30 | 0.077 | 2.31 | Btu/hr-sf | 392 | 905.52 | 193 | 445.83 | 99 | 228.69 | 100 | 231 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W3 | Attic | 55 | 0.077 | 4.235 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W3 | Kneewall | 55 | 0.077 | 4.235 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Roof | R1 | Ceiling | 55 | 0.026 | 1.43 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| R2 | Vaulted | 55 | 0.053 | 2.915 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Floor | F1 | Crawl/Uncon. | 11 | 0.053 | 0.583 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| F1 | Garage | 30 | 0.053 | 1.59 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| F2 | Slab | 0 | 0.1 | 0 | Btu/hr-sf | 1281 | 0 | 213 | 0 | 65 | 0 | 46 | 0 | 240 | 0 | 178 | 0 | 290 | 0 | 57 | 0 | 192 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Internal |  | People |  |  | 255 | Btu/hr-sf | 2 | 510 |  | - |  | - |  | - |  | - |  | - | 1 | 255 |  | - | 1 | 255 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
|  | Lights |  |  | 3.413 | Btu/hr-sf | 640.5 | 2191.146 | 106.5 | 365.191 | 32.5 | 112.629 | 23 | 78.499 | 120 | 409.56 | 89 | 303.757 | 145 | 494.885 | 28.5 | 98.977 | 96 | 327.648 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
|  | Appliances |  |  | 3.413 | Btu/hr-sf | 930 | 3174.09 |  | - |  | - |  | - | 680 | 2320.84 |  | - | 250 | 853.25 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Volume | [5 empty] | CF | 11700 | 0 | 1917 | 0 | 585 | 0 | 414 | 0 | 2160 | 0 | 1602 | 0 | 2610 | 0 | 684 | 0 | 1728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Infiltration (Tight) |  |  | 0.25 | ACH | 0.09 | Btu/hr-sf | 0 | 1053 | 0 | 172.53 | 0 | 52.65 | 0 | 37.26 | 0 | 194.4 | 0 | 144.18 | 0 | 234.9 | 0 | 61.56 | 0 | 155.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Subtotal (Btu/hr) | [7 empty] | 12883.7405 |  | 1218.1637 |  | 660.969 |  | 403.431 |  | 3816.9786 |  | 1705.604 |  | 3522.1986 |  | 262.6101 |  | 1293.7856 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
Safety Factor |  |  |  |  | 10% |  |  | 1288.3741 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Sensible Cooling Load (Btu/hr) | [7 empty] | 14172.1146 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Nominal Tons Required (75% sens. Cap.) | [7 empty] | 1.5747 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
System Selection |  |  | 2 | Tons | Space CFM |  |  | 800 |  | 75.6404 |  | 41.0421 |  | 25.0506 |  | 237.0106 |  | 105.9074 |  | 218.7066 |  | 16.3065 |  | 80.336 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
Components |  |  | Detla T (°F) | U-Value (Btu/hr-sf-°F) | Heating Load Factor |  | Entire House |  | Foyer & Hall |  | Garage Entry |  | Pantry |  | Kitchen |  | Dining |  | Great Room |  | Bath 4 |  | Bed 6
| Type | Description |  |  |  |  | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr
Glass | G1 |  | 54 | 0.32 | 17.28 | Btu/hr-sf | 155 | 2678.4 | 10 | 172.8 |  | - |  | - | 16 | 276.48 | 40 | 691.2 | 45 | 777.6 | 8 | 138.24 | 36 | 622.08 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G2 |  | 54 | 0 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G3 |  | 54 | 0 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Door | D1 |  | 54 | 0.5 | 27 | Btu/hr-sf | 10 | 270 | 10 | 270 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| D2 |  | 54 | 0.5 | 27 | Btu/hr-sf | 17.8 | 480.6 |  | - | 17.8 | 480.6 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Walls | W1 |  | 54 | 0.077 | 4.158 | Btu/hr-sf | 1057 | 4395.006 | 40 | 166.32 |  | - | 46 | 191.268 | 298 | 1239.084 | 58 | 241.164 | 296 | 1230.768 | 55 | 228.69 | 264 | 1097.712 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W2 |  | 54 | 0.067 | 3.618 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W3 |  | 54 | 0.077 | 4.158 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Partition | 27 | 0.077 | 2.079 | Btu/hr-sf | 392 | 814.968 | 193 | 401.247 | 99 | 205.821 | 100 | 207.9 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W2 | Grade | 27 | 0.067 | 1.809 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Roof | R1 |  | 54 | 0.026 | 1.404 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| R2 |  | 54 | 0.053 | 2.862 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Floor | F1 |  | 54 | 0.053 | 2.862 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| F2 | Slab | 27 | 0.1 | 2.7 | Btu/hr-sf | 1281 | 3458.7 | 213 | 575.1 | 65 | 175.5 | 46 | 124.2 | 240 | 648 | 178 | 480.6 | 290 | 783 | 57 | 153.9 | 192 | 518.4 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Infiltration |  |  | 0.25 | ACH | 0.24 | Btu/hr-sf | 1281 | 2808 | 213 | 460.08 | 65 | 140.4 | 46 | 99.36 | 240 | 518.4 | 178 | 384.48 | 290 | 626.4 | 57 | 164.16 | 192 | 414.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Subtotal | [7 empty] | 14905.674 |  | 2045.547 |  | 1002.321 |  | 622.728 |  | 2681.964 |  | 1797.444 |  | 3417.768 |  | 684.99 |  | 2652.912
Safety Factor |  |  |  |  | 15 | % |  | 2235.8511
Heat Loss |  |  | Nominal Size |  | 1.5036 | tons |  | 17141.5251
Minimum Heater Size | [7 empty] | 5.0224
System Selection |  |  | 5 | kW | Htg CFM |  |  | 800 |  | 109.7862 |  | 53.7954 |  | 33.4223 |  | 143.9433 |  | 96.4703 |  | 183.4345 |  | 36.764 |  | 142.384

## Unit 1 b
Project |  |  | Reserve at Gum Springs ; Century Communities | [7 empty] | Date: | 2017-09-20 | [5 empty] | Typical Ceiling Height |  |  | 8
Location |  |  | Jefferson, GA | [7 empty] | By:
Description |  |  | Guava - A2/B2, Slab, Bed 5, Bed 6, Optional Covered Patio | [7 empty] | Level(s): | Upstairs |  |  | Unit 1 b |  |  | Kneewall Height |  |  | 1
|  |  | Square Feet |  | 1733 | Volume | 13864 | Sf/Ton | 866.5 |  | SEER | 14
[7 empty] | Ceiling Height |  | 18 |  | 8 |  | 8 |  | 8 |  | 8 |  | 8 |  | 8 |  | 8 |  | 8 |  | 8 |  | 8 |  | 8 |  | 8 |  | 8 |  | 8
Components |  |  | CLTD (°F) | U-Value (Btu/hr-sf-°F) | Cooling Load Factor |  | Entire House |  | Stairs |  | Hallway |  | Bath 3 |  | Bed 4 |  | Bed 4 WIC |  | Bed 5 |  | Bed 3 |  | Bed 3 WIC |  | Bed 2 & WIC |  | Bath 2 |  | Owner WIC |  | Owner Bath |  | Owner Suite |  | Laundry
| Type | Description |  |  |  |  | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr
Glass | G1 | North | Right | (E) | 5.8773 | Btu/hr-sf | 15 | 88.159 | 15 | 88.159 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | Northeast |  | (SE) | 7.5027 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | East | Front | (S) | 12.63 | Btu/hr-sf | 60 | 757.8 |  | - |  | - |  | - | 30 | 378.9 |  | - | 15 | 189.45 | 15 | 189.45 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | SouthEast |  | (SW) | 13.9472 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | South | Left | (W) | 15.5451 | Btu/hr-sf | 15 | 233.1763 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - | 15 | 233.1763 |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | SouthWest |  | (NW) | 25.896 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | West | Back | (N) | 28.8737 | Btu/hr-sf | 45 | 1299.3176 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - | 45 | 1299.3176 |  | - |  | -
| G1 | NorthWest |  | (NE) | 17.9826 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | Sky Light |  |  | 55 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | Shaded |  |  | 5.8773 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Door | D1 | Door 1 | 21 | 0.5 | 10.5 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| D2 | Door 2 | 30 | 0.5 | 15 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Above Grade Walls | W1 | North | 13 | 0.077 | 1.001 | Btu/hr-sf | 473 | 473.473 | 123 | 123.123 |  | - | 74 | 74.074 | 113 | 113.113 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - | 163 | 163.163 |  | - |  | -
| W1 | Northeast | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | East | 23 | 0.077 | 1.771 | Btu/hr-sf | 291 | 515.361 |  | - |  | - |  | - | 90 | 159.39 |  | - | 98 | 173.558 | 103 | 182.413 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthEast | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | South | 16 | 0.077 | 1.232 | Btu/hr-sf | 401 | 494.032 |  | - |  | - |  | - | 20 | 24.64 |  | - |  | - | 119 | 146.608 | 43 | 52.976 | 96 | 118.272 |  | - | 123 | 151.536 |  | - |  | - |  | - |  | -
| W1 | SouthWest | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | West | 23 | 0.077 | 1.771 | Btu/hr-sf | 306 | 541.926 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - | 96 | 170.016 | 104 | 184.184 | 106 | 187.726 |  | - |  | -
| W1 | NorthWest | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Basement Walls | W1 | North | 13 | 0.077 | 1.001 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Northeast | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | East | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthEast | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | South | 16 | 0.077 | 1.232 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthWest | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | West | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | NorthWest | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Other | W2 | Grade | 0 | 0.067 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Partition | 10 | 0.077 | 0.77 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Garage | 30 | 0.077 | 2.31 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W3 | Attic | 55 | 0.077 | 4.235 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W3 | Kneewall | 55 | 0.077 | 4.235 | Btu/hr-sf | 29 | 122.815 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - | 29 | 122.815 |  | - |  | - |  | -
Roof | R1 | Ceiling | 55 | 0.026 | 1.43 | Btu/hr-sf | 1733 | 2478.19 | 74 | 105.82 | 155 | 221.65 | 46 | 65.78 | 174 | 248.82 | 22 | 31.46 | 177 | 253.11 | 177 | 253.11 | 29 | 41.47 | 183 | 261.69 | 63 | 90.09 | 145 | 207.35 | 138 | 197.34 | 282 | 403.26 | 68 | 97.24 |  | -
| R2 | Vaulted | 55 | 0.053 | 2.915 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Floor | F1 | Crawl/Uncon. | 11 | 0.053 | 0.583 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| F1 | Garage | 30 | 0.053 | 1.59 | Btu/hr-sf | 397 | 631.23 |  | - | 55 | 87.45 |  | - |  | - |  | - | 90 | 143.1 | 177 | 281.43 | 29 | 46.11 | 37 | 58.83 | 9 | 14.31 |  | - |  | - |  | - |  | - |  | -
| F2 | Slab | 0 | 0.1 | 0 | Btu/hr-sf | 66 | 0 | 66 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Internal |  | People |  |  | 255 | Btu/hr-sf | 5 | 1275 |  | - |  | - |  | - | 1 | 255 |  | - | 1 | 255 | 1 | 255 |  | - | 1 | 255 |  | - |  | - |  | - | 1 | 255 |  | - |  | -
|  | Lights |  |  | 3.413 | Btu/hr-sf | 870 | 2969.31 | 37 | 126.281 | 77.5 | 266.214 | 23 | 78.499 | 87 | 296.931 | 11 | 37.543 | 88.5 | 303.757 | 88.5 | 303.757 | 14.5 | 51.195 | 91.5 | 313.996 | 31.5 | 109.216 | 72.5 | 249.149 | 69 | 235.497 | 141 | 481.233 | 34 | 116.042 |  | -
|  | Appliances |  |  | 3.413 | Btu/hr-sf | 200 | 682.6 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - | 200 | 682.6 |  | -
Volume | [5 empty] | CF | 13864 | 0 | 1332 |  | 1240 |  | 368 |  | 1392 |  | 176 |  | 1416 |  | 1416 |  | 232 |  | 1464 |  | 504 |  | 1160 |  | 1104 |  | 2256 |  | 544 |  | 0
Infiltration (Tight) |  |  | 0.25 | ACH | 0.09 | Btu/hr-sf | 0 | 1247.76 |  | 119.88 |  | 111.6 |  | 33.12 |  | 125.28 |  | 15.84 |  | 127.44 |  | 127.44 |  | 20.88 |  | 131.76 |  | 45.36 |  | 104.4 |  | 99.36 |  | 203.04 |  | 48.96 |  | 0
Subtotal (Btu/hr) | [7 empty] | 13810.1499 |  | 563.263 |  | 686.914 |  | 251.473 |  | 1602.074 |  | 84.843 |  | 1445.415 |  | 1739.208 |  | 212.631 |  | 1372.7243 |  | 258.976 |  | 882.451 |  | 839.196 |  | 2992.7396 |  | 944.842 |  | 0
Safety Factor |  |  |  |  | 10% |  |  | 1381.015 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Sensible Cooling Load (Btu/hr) | [7 empty] | 15191.1649 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Nominal Tons Required (75% sens. Cap.) | [7 empty] | 1.6879 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
System Selection |  |  | 2 | Tons | Space CFM |  |  | 800 |  | 32.6289 |  | 39.7918 |  | 14.5674 |  | 92.8056 |  | 4.9148 |  | 83.7306 |  | 100.7496 |  | 12.3174 |  | 79.5197 |  | 15.0021 |  | 51.119 |  | 48.6133 |  | 173.3646 |  | 54.7332 |  | 0
Components |  |  | Detla T (°F) | U-Value (Btu/hr-sf-°F) | Heating Load Factor |  | Entire House |  | Stairs |  | Hallway |  | Bath 3 |  | Bed 4 |  | Bed 4 WIC |  | Bed 5 |  | Bed 3 |  | Bed 3 WIC |  | Bed 2 & WIC |  | Bath 2 |  | Owner WIC |  | Owner Bath |  | Owner Suite |  | Laundry
| Type | Description |  |  |  |  | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr
Glass | G1 |  | 54 | 0.32 | 17.28 | Btu/hr-sf | 135 | 2332.8 | 15 | 259.2 |  | - |  | - | 30 | 518.4 |  | - | 15 | 259.2 | 15 | 259.2 |  | - | 15 | 259.2 |  | - |  | - |  | - | 45 | 777.6 |  | - |  | -
| G2 |  | 54 | 0 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G3 |  | 54 | 0 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Door | D1 |  | 54 | 0.5 | 27 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| D2 |  | 54 | 0.5 | 27 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Walls | W1 |  | 54 | 0.077 | 4.158 | Btu/hr-sf | 1471 | 6116.418 | 123 | 511.434 |  | - | 74 | 307.692 | 223 | 927.234 |  | - | 98 | 407.484 | 222 | 923.076 | 43 | 178.794 | 96 | 399.168 |  | - | 219 | 910.602 | 104 | 432.432 | 269 | 1118.502 |  | - |  | -
| W2 |  | 54 | 0.067 | 3.618 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W3 |  | 54 | 0.077 | 4.158 | Btu/hr-sf | 29 | 120.582 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - | 29 | 120.582 |  | - |  | - |  | -
| W1 | Partition | 27 | 0.077 | 2.079 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W2 | Grade | 27 | 0.067 | 1.809 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Roof | R1 |  | 54 | 0.026 | 1.404 | Btu/hr-sf | 1733 | 2433.132 | 74 | 103.896 | 155 | 217.62 | 46 | 64.584 | 174 | 244.296 | 22 | 30.888 | 177 | 248.508 | 177 | 248.508 | 29 | 40.716 | 183 | 256.932 | 63 | 88.452 | 145 | 203.58 | 138 | 193.752 | 282 | 395.928 | 68 | 95.472 |  | -
| R2 |  | 54 | 0.053 | 2.862 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Floor | F1 |  | 54 | 0.053 | 2.862 | Btu/hr-sf | 397 | 1136.214 |  | - | 55 | 157.41 |  | - |  | - |  | - | 90 | 257.58 | 177 | 506.574 | 29 | 82.998 | 37 | 105.894 | 9 | 25.758 |  | - |  | - |  | - |  | - |  | -
| F2 | Slab | 27 | 0.1 | 2.7 | Btu/hr-sf | 66 | 178.2 | 66 | 178.2 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Infiltration |  |  | 0.25 | ACH | 0.24 | Btu/hr-sf | 463 | 3327.36 | 66 | 319.68 | 55 | 297.6 | 0 | 88.32 | 0 | 334.08 | 0 | 42.24 | 90 | 339.84 | 177 | 339.84 | 29 | 55.68 | 37 | 351.36 | 9 | 120.96 | 0 | 278.4 | 0 | 264.96 | 0 | 541.44 | 0 | 130.56 | 0 | 0
Subtotal | [7 empty] | 15644.706 |  | 1372.41 |  | 672.63 |  | 460.596 |  | 2024.01 |  | 73.128 |  | 1512.612 |  | 2277.198 |  | 358.188 |  | 1372.554 |  | 235.17 |  | 1392.582 |  | 1011.726 |  | 2833.47 |  | 226.032
Safety Factor |  |  |  |  | 15 | % |  | 2346.7059
Heat Loss |  |  | Nominal Size |  | 1.5782 | tons |  | 17991.4119
Minimum Heater Size | [7 empty] | 5.2714
System Selection |  |  | 5 | kW | Htg CFM |  |  | 800 |  | 70.1789 |  | 34.3953 |  | 23.5528 |  | 103.4988 |  | 3.7394 |  | 77.3482 |  | 116.4457 |  | 18.3161 |  | 70.1862 |  | 12.0255 |  | 71.2104 |  | 51.7351 |  | 144.8909 |  | 11.5583

## Unit 2 a
Project |  |  | Reserve at Gum Springs ; Century Communities | [7 empty] | Date: | 2017-09-20 | [5 empty] | Typical Ceiling Height |  |  | 9
Location |  |  | Jefferson, GA | [7 empty] | By:
Description |  |  | Guava - A2/B2, Slab, Bed 5, Bed 6, Optional Covered Patio | [7 empty] | Level(s): | First Floor |  |  | Unit 2 a |  |  | Kneewall Height |  |  | 1
|  |  | Square Feet |  | 0 | Volume | 0 | Sf/Ton | 0 |  | SEER | 14
[7 empty] | Ceiling Height |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9
Components |  |  | CLTD (°F) | U-Value (Btu/hr-sf-°F) | Cooling Load Factor |  | Entire House
| Type | Description |  |  |  |  | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr
Glass | G1 | North | Right | (E) | 5.8773 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | Northeast |  | (SE) | 7.5027 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | East | Front | (S) | 12.63 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | SouthEast |  | (SW) | 13.9472 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | South | Left | (W) | 15.5451 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | SouthWest |  | (NW) | 25.896 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | West | Back | (N) | 28.8737 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | NorthWest |  | (NE) | 17.9826 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | Sky Light |  |  | 55 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | Shaded |  |  | 5.8773 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Door | D1 | Door 1 | 21 | 0.5 | 10.5 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| D2 | Door 2 | 30 | 0.5 | 15 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Above Grade Walls | W1 | North | 13 | 0.077 | 1.001 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Northeast | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | East | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthEast | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | South | 16 | 0.077 | 1.232 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthWest | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | West | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | NorthWest | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Basement Walls | W1 | North | 13 | 0.077 | 1.001 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Northeast | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | East | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthEast | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | South | 16 | 0.077 | 1.232 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthWest | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | West | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | NorthWest | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Other | W2 | Grade | 0 | 0.067 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Partition | 10 | 0.077 | 0.77 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Garage | 30 | 0.077 | 2.31 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W3 | Attic | 55 | 0.077 | 4.235 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W3 | Kneewall | 55 | 0.077 | 4.235 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Roof | R1 | Ceiling | 55 | 0.026 | 1.43 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| R2 | Vaulted | 55 | 0.053 | 2.915 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Floor | F1 | Crawl/Uncon. | 11 | 0.053 | 0.583 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| F1 | Garage | 30 | 0.053 | 1.59 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| F2 | Slab | 0 | 0.1 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Internal |  | People |  |  | 255 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
|  | Lights |  |  | 3.413 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
|  | Appliances |  |  | 3.413 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Volume | [5 empty] | CF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Infiltration (Tight) |  |  | 0.25 | ACH | 0.09 | Btu/hr-sf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Subtotal (Btu/hr) | [7 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
Safety Factor |  |  |  |  | 10% |  |  | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Sensible Cooling Load (Btu/hr) | [7 empty] | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Nominal Tons Required (75% sens. Cap.) | [7 empty] | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
System Selection |  |  | 1.5 | Tons | Space CFM |  |  | 600 |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0!
Components |  |  | Detla T (°F) | U-Value (Btu/hr-sf-°F) | Heating Load Factor |  | Entire House
| Type | Description |  |  |  |  | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr
Glass | G1 |  | 54 | 0.32 | 17.28 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G2 |  | 54 | 0 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G3 |  | 54 | 0 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Door | D1 |  | 54 | 0.5 | 27 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| D2 |  | 54 | 0.5 | 27 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Walls | W1 |  | 54 | 0.077 | 4.158 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W2 |  | 54 | 0.067 | 3.618 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W3 |  | 54 | 0.077 | 4.158 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Partition | 27 | 0.077 | 2.079 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W2 | Grade | 27 | 0.067 | 1.809 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Roof | R1 |  | 54 | 0.026 | 1.404 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| R2 |  | 54 | 0.053 | 2.862 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Floor | F1 |  | 54 | 0.053 | 2.862 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| F2 | Slab | 27 | 0.1 | 2.7 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Infiltration |  |  | 0.25 | ACH | 0.24 | Btu/hr-sf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Subtotal | [7 empty] | 0
Safety Factor |  |  |  |  | 15 | % |  | 0
Heat Loss |  |  | Nominal Size |  | 0 | tons |  | 0
Minimum Heater Size | [7 empty] | 0
System Selection |  |  | 5 | kW | Htg CFM |  |  | 600

## Unit 2 b
Project |  |  | Reserve at Gum Springs ; Century Communities | [7 empty] | Date: | 2017-09-20 | [5 empty] | Typical Ceiling Height |  |  | 9
Location |  |  | Jefferson, GA | [7 empty] | By:
Description |  |  | Guava - A2/B2, Slab, Bed 5, Bed 6, Optional Covered Patio | [7 empty] | Level(s): | First Floor |  |  | Unit 2 b |  |  | Kneewall Height |  |  | 1
|  |  | Square Feet |  | 0 | Volume | 0 | Sf/Ton | 0 |  | SEER | 14
[7 empty] | Ceiling Height |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9
Components |  |  | CLTD (°F) | U-Value (Btu/hr-sf-°F) | Cooling Load Factor |  | Entire House
| Type | Description |  |  |  |  | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr
Glass | G1 | North | Right | (E) | 5.8773 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | Northeast |  | (SE) | 7.5027 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | East | Front | (S) | 12.63 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | SouthEast |  | (SW) | 13.9472 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | South | Left | (W) | 15.5451 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | SouthWest |  | (NW) | 25.896 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | West | Back | (N) | 28.8737 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | NorthWest |  | (NE) | 17.9826 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | Sky Light |  |  | 55 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | Shaded |  |  | 5.8773 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Door | D1 | Door 1 | 21 | 0.5 | 10.5 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| D2 | Door 2 | 30 | 0.5 | 15 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Above Grade Walls | W1 | North | 13 | 0.077 | 1.001 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Northeast | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | East | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthEast | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | South | 16 | 0.077 | 1.232 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthWest | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | West | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | NorthWest | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Basement Walls | W1 | North | 13 | 0.077 | 1.001 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Northeast | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | East | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthEast | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | South | 16 | 0.077 | 1.232 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthWest | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | West | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | NorthWest | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Other | W2 | Grade | 0 | 0.067 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Partition | 10 | 0.077 | 0.77 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Garage | 30 | 0.077 | 2.31 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W3 | Attic | 55 | 0.077 | 4.235 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W3 | Kneewall | 55 | 0.077 | 4.235 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Roof | R1 | Ceiling | 55 | 0.026 | 1.43 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| R2 | Vaulted | 55 | 0.053 | 2.915 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Floor | F1 | Crawl/Uncon. | 11 | 0.053 | 0.583 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| F1 | Garage | 30 | 0.053 | 1.59 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| F2 | Slab | 0 | 0.1 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Internal |  | People |  |  | 255 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
|  | Lights |  |  | 3.413 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
|  | Appliances |  |  | 3.413 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Volume | [5 empty] | CF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Infiltration (Tight) |  |  | 0.25 | ACH | 0.09 | Btu/hr-sf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Subtotal (Btu/hr) | [7 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
Safety Factor |  |  |  |  | 10% |  |  | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Sensible Cooling Load (Btu/hr) | [7 empty] | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Nominal Tons Required (75% sens. Cap.) | [7 empty] | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
System Selection |  |  | 1.5 | Tons | Space CFM |  |  | 600 |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0!
Components |  |  | Detla T (°F) | U-Value (Btu/hr-sf-°F) | Heating Load Factor |  | Entire House
| Type | Description |  |  |  |  | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr
Glass | G1 |  | 54 | 0.32 | 17.28 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G2 |  | 54 | 0 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G3 |  | 54 | 0 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Door | D1 |  | 54 | 0.5 | 27 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| D2 |  | 54 | 0.5 | 27 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Walls | W1 |  | 54 | 0.077 | 4.158 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W2 |  | 54 | 0.067 | 3.618 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W3 |  | 54 | 0.077 | 4.158 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Partition | 27 | 0.077 | 2.079 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W2 | Grade | 27 | 0.067 | 1.809 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Roof | R1 |  | 54 | 0.026 | 1.404 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| R2 |  | 54 | 0.053 | 2.862 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Floor | F1 |  | 54 | 0.053 | 2.862 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| F2 | Slab | 27 | 0.1 | 2.7 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Infiltration |  |  | 0.25 | ACH | 0.24 | Btu/hr-sf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Subtotal | [7 empty] | 0
Safety Factor |  |  |  |  | 15 | % |  | 0
Heat Loss |  |  | Nominal Size |  | 0 | tons |  | 0
Minimum Heater Size | [7 empty] | 0
System Selection |  |  | 5 | kW | Htg CFM |  |  | 600

## Unit 3 a
Project |  |  | Reserve at Gum Springs ; Century Communities | [7 empty] | Date: | 2017-09-20 | [5 empty] | Typical Ceiling Height |  |  | 9
Location |  |  | Jefferson, GA | [7 empty] | By:
Description |  |  | Guava - A2/B2, Slab, Bed 5, Bed 6, Optional Covered Patio | [7 empty] | Level(s): | First Floor |  |  | Unit 3 a |  |  | Kneewall Height |  |  | 1
|  |  | Square Feet |  | 0 | Volume | 0 | Sf/Ton | 0 |  | SEER | 14
[7 empty] | Ceiling Height |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9 |  | 9
Components |  |  | CLTD (°F) | U-Value (Btu/hr-sf-°F) | Cooling Load Factor |  | Entire House
| Type | Description |  |  |  |  | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr
Glass | G1 | North | Right | (E) | 5.8773 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | Northeast |  | (SE) | 7.5027 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | East | Front | (S) | 12.63 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | SouthEast |  | (SW) | 13.9472 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | South | Left | (W) | 15.5451 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | SouthWest |  | (NW) | 25.896 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | West | Back | (N) | 28.8737 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | NorthWest |  | (NE) | 17.9826 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | Sky Light |  |  | 55 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | Shaded |  |  | 5.8773 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Door | D1 | Door 1 | 21 | 0.5 | 10.5 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| D2 | Door 2 | 30 | 0.5 | 15 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Above Grade Walls | W1 | North | 13 | 0.077 | 1.001 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Northeast | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | East | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthEast | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | South | 16 | 0.077 | 1.232 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthWest | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | West | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | NorthWest | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Basement Walls | W1 | North | 13 | 0.077 | 1.001 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Northeast | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | East | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthEast | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | South | 16 | 0.077 | 1.232 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthWest | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | West | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | NorthWest | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Other | W2 | Grade | 0 | 0.067 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Partition | 10 | 0.077 | 0.77 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Garage | 30 | 0.077 | 2.31 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W3 | Attic | 55 | 0.077 | 4.235 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W3 | Kneewall | 55 | 0.077 | 4.235 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Roof | R1 | Ceiling | 55 | 0.026 | 1.43 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| R2 | Vaulted | 55 | 0.053 | 2.915 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Floor | F1 | Crawl/Uncon. | 11 | 0.053 | 0.583 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| F1 | Garage | 30 | 0.053 | 1.59 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| F2 | Slab | 0 | 0.1 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Internal |  | People |  |  | 255 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
|  | Lights |  |  | 3.413 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
|  | Appliances |  |  | 3.413 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Volume | [5 empty] | CF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Infiltration (Tight) |  |  | 0.25 | ACH | 0.09 | Btu/hr-sf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Subtotal (Btu/hr) | [7 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
Safety Factor |  |  |  |  | 10% |  |  | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Sensible Cooling Load (Btu/hr) | [7 empty] | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Nominal Tons Required (75% sens. Cap.) | [7 empty] | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
System Selection |  |  | 1.5 | Tons | Space CFM |  |  | 600 |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0!
Components |  |  | Detla T (°F) | U-Value (Btu/hr-sf-°F) | Heating Load Factor |  | Entire House
| Type | Description |  |  |  |  | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr
Glass | G1 |  | 54 | 0.32 | 17.28 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G2 |  | 54 | 0 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G3 |  | 54 | 0 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Door | D1 |  | 54 | 0.5 | 27 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| D2 |  | 54 | 0.5 | 27 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Walls | W1 |  | 54 | 0.077 | 4.158 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W2 |  | 54 | 0.067 | 3.618 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W3 |  | 54 | 0.077 | 4.158 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Partition | 27 | 0.077 | 2.079 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W2 | Grade | 27 | 0.067 | 1.809 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Roof | R1 |  | 54 | 0.026 | 1.404 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| R2 |  | 54 | 0.053 | 2.862 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Floor | F1 |  | 54 | 0.053 | 2.862 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| F2 | Slab | 27 | 0.1 | 2.7 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Infiltration |  |  | 0.25 | ACH | 0.24 | Btu/hr-sf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Subtotal | [7 empty] | 0
Safety Factor |  |  |  |  | 15 | % |  | 0
Heat Loss |  |  | Nominal Size |  | 0 | tons |  | 0
Minimum Heater Size | [7 empty] | 0
System Selection |  |  | 5 | kW | Htg CFM |  |  | 600

## Glass CLF Calculation
[7 empty] | 2022 | 2019 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2021 | 2022 | 2022 | 2022 | 2020 | 2022 | 2018 | 2017 | 2017 | 2021 | 2020 | 2021 | 2017 | 2019 | 2019 | 2022 | 2023 | 2020
[7 empty] | Hoschton | Hoschton | Jefferson | Oakwood | Oakwood | Oakwood | Oakwood | Oakwood | Gainesville | Jefferson | Jefferson | Jefferson | Jefferson | Jefferson | Jefferson | Hoschton | Homer | Homer | Homer | Buford | Buford | Statham | Statham | Bethlehem | Dacula | Dacula
Window | TableGLF | Corrected | Applied GLF | Mystery CF |  | CLF | Sidney | Chelsea | 2831 | Sally - A Slab | Hawthorn II - Slab |  | Pembrooke | Chestnut | Chadwick | Reed | 1755 | 1921 | R-7 | Nassick | Devon Gales | Abbeyville | Englemoore | Nelson | Nicklaus | Dakota D | Sienna | Ellijay | Finley | Bradley | Ruth Ann | Monroe
NorthWest | 59 |  | 59 | 0.56 | 0.1232 | 17.9826 | 17 | 22 | 25 | 21 | 21 | 21 | 21 | 21 | 18 | 17 | 25 | 25 | 18 | 17 | 23 | 21.68 | 21 | 23 | 23 | 18 | 18 | 21 | 21 | 21 | 18 | 21
North | 34 |  | 34 | 0.1765 | 0.03883 | 5.8773 | 6 | 7 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 6 | 6 | 6 | 7 | 6 | 7 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 6
NorthEast | 59 |  | 59 | 0.156 | 0.03432 | 7.5027 | 7 | 9 | 9 | 8 | 8 | 8 | 8 | 8 | 7 | 9 | 9 | 9 | 7 | 7 | 9 | 8.69 | 8 | 9 | 9 | 8 | 8 | 8 | 8 | 8 | 8 | 8
East | 81 |  | 81 | 0.25 | 0.055 | 12.63 | 12 | 16 | 17 | 15 | 15 | 15 | 15 | 15 | 12 | 12 | 17 | 17 | 13 | 12 | 16 | 15 | 15 | 16 | 16 | 13 | 13 | 15 | 15 | 15 | 13 | 15
SouthEast | 73 |  | 73 | 0.32 | 0.0704 | 13.9472 | 13 | 17 | 19 | 16 | 16 | 16 | 16 | 16 | 14 | 13 | 19 | 19 | 14 | 13 | 17 | 16.66 | 16 | 18 | 18 | 14 | 14 | 16 | 16 | 16 | 14 | 16
South | 81 | 63.18 | 63.18 | 0.432 | 0.09504 | 15.5451 | 14 | 19 | 21 | 18 | 18 | 18 | 18 | 18 | 15 | 15 | 21 | 21 | 15 | 15 | 19 | 18 | 18 | 20 | 20 | 16 | 16 | 18 | 18 | 18 | 16 | 18
SouthWest | 73 | 56.94 | 56.94 | 0.9 | 0.198 | 25.896 | 24 | 32 | 37 | 31 | 31 | 31 | 31 | 31 | 26 | 25 | 37 | 37 | 26 | 25 | 34 | 31.22 | 31 | 34 | 34 | 26 | 26 | 31 | 31 | 31 | 26 | 31
West | 50 |  | 50 | 1.18 | 0.2596 | 28.8737 | 27 | 36 | 42 | 35 | 35 | 35 | 35 | 35 | 29 | 28 | 42 | 42 | 29 | 28 | 38 | 35 | 35 | 39 | 39 | 29 | 29 | 35 | 35 | 35 | 29 | 35
|  |  |  | U |  | 0.32 | 0.32 | 0.35 | 0.31 | [8 empty] | 0.31 | 0.31 | 0.3 | 0.3 | 0.35 | 0.33 | 0.33 | 0.33 | 0.35 | 0.35 | 0.33
|  |  |  | SHGC |  | 0.22 | 0.2 | 0.28 | 0.33 | [8 empty] | 0.33 | 0.22 | 0.21 | 0.3 | 0.27 | 0.27 | 0.3 | 0.3 | 0.22 | 0.22 | 0.27
|  |  |  | GLF correction |  | -0.22 | [5 empty] | CLTD | U | SHGC
Door
D1 | [5 empty] | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
D2 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Wall
NorthWest | [5 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
North | [5 empty] | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
NorthEast | [5 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
East | [5 empty] | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23
SouthEast | [5 empty] | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
South | [5 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
SouthWest | [5 empty] | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
West | [5 empty] | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23
Attic Insulation Types
R-30 Blown
R-30 Batt | [11 empty] | SCa | SCt | GLFt | Ut | Ua | Dt | DR | To | Ta
R-38 Blown | [11 empty] | 0.5 | 0.45 | 81 | 0.55 | 0.32 | 10.8 | 18.4 | 95 | 85.8
R-45 Blown
R-49 Blown
R-50 Blown | [11 empty] | 86.856 | 0
R-21 Spray Foam
Unit 1 a
Unit 1 b
Unit 2 a
Unit 2 b
Unit 3 a
Unit 3 b
Unit 4
Unit 5