## Summary
Project |  | Carillon | [11 empty] | Date: |  | 2017-09-20
Location |  | Lawrenceville, GA | [11 empty] | By: |  | WHM
Description |  | Millhaven GL | [11 empty] | House Faces: |  |  | Worst | South
BUILDING DATA | [5 empty] | DESIGN CONDITIONS | [8 empty] | ENERGY CALCULATIONS
Typical Ceiling Height |  |  | 8.5 | ft |  |  |  | Summer |  | Winter
Floor Area |  |  | 2512 | ft2 |  | Outdoor |  | 95 | °Fdb | 18 | °Fdb
Volume |  |  | 21928 | ft3 |  | Indoor |  | 75 | °Fdb | 72 | °Fdb
Building Tightness |  |  | Tight | 0.25 |  | Delta T |  | 20 | °Fdb | 54 | °Fdb
[6 empty] | Range |  | 17.3 | °Fdb
Construction Descriptions
Walls / Partitions | # | U-Value | Description / Notes
| W1 | 0.077 | Above Grade |  |  |  |  | 2x4 |  |  |  | R-13 batt
| W2 | 0.067 | Basement |  |  |  |  | Concrete + 2x4 |  |  |  | R-13 batt
| W3 | 0.053 | Attic |  |  |  |  | 2x6 |  |  |  | R19 batt
Doors | # | U-Value | Description / Notes
| D1 | 0.5 | Exterior Door | [8 empty] | R-2
| D2 | 0.5 | Garage Door | [8 empty] | R-2
Roofs | # | U-Value | Description / Notes
| R1 | 0.026 | Flat Ceiling |  |  |  |  | Truss |  |  |  | R-38 Blown
| R2 | 0.26 | Vaulted |  |  |  |  | Truss |  |  |  | R-38 Blown
Floors | # | U-Value | Description / Notes
| F1 | 0.053 | Framed |  |  |  |  | I-Joist |  |  |  | R-19 batt
| F2 | 0.1 | Slab | [8 empty] | None
Glass | # | Glass Type |  |  |  |  | Windows |  |  | U-Value |  | Internal Shading |  |  |  |  | Notes
| G1 | Double Insulated |  |  |  |  | All Types |  |  | 0.35 |  | Blinds/ Draperies |  |  |  |  | SHGC | 0.22
G2
G3
Load Summary
[5 empty] | Unit 1 |  |  | Unit 2 |  |  |  |  | Unit 3
[5 empty] | Cooling | Heating |  | Cooling |  | Heating |  |  | Cooling |  |  | Heating
Sensible Load |  |  |  | btu/hr | 24842.3353 | 30169.2219 |  | 0 |  | 0
Minimum Nominal Capacity |  |  |  | tons | 2.7603 | 8.8395 | kW | 0 |  | 0 | kW
Load Density |  |  |  | sf/ton | 910.0594 | 3.5189 | W/sf
Floor Area Served |  |  |  | sf | 2512
System Size |  |  |  | tons | 3.5 | 10 | kW
Leaving Air Temperature |  |  |  | °f | 57.2 | 96.3
Installed Capacity |  |  |  | sf/ton | 717.7143 | 3.9809 | w/sf

## Rooms Walls and Glass
Room Name |  |  | Entry | Family | PS WIC | PS Bath | PS Bed | Breakfast / Kitchen | Powder | Stairs | Loft | Master Bed | Master Bath | Master WIC | Bed 3 WIC | Bed 3 | Bath2 | Bed 4 | Hallway | Laundry
Front Faces: | NorthEast |  | Unit 1 b | Unit 1 b | Unit 1 b | Unit 1 b | Unit 1 b | Unit 1 b | Unit 1 b | Unit 1 a | Unit 1 a | Unit 1 a | Unit 1 a | Unit 1 a | Unit 1 a | Unit 1 a | Unit 1 a | Unit 1 a | Unit 1 a | Unit 1 a
People |  |  |  | 1 |  |  | 1 |  |  |  | 1 | 1 |  |  |  | 1 |  | 1
Appliances |  |  |  | 250 |  |  |  | 680 |  |  | 250 | [8 empty] | 200
Glass & Doors |  |  | Glass & Doors
Direction | Facing | Type | Entry | Family | PS WIC | PS Bath | PS Bed | Breakfast / Kitchen | Powder | Stairs | Loft | Master Bed | Master Bath | Master WIC | Bed 3 WIC | Bed 3 | Bath2 | Bed 4 | Hallway | Laundry | 0 | 0 | 0 | 0 | 0 | 0 | 0
NorthWest | Right | G1 |  | 36 | [6 empty] | 30
North |  | G1
NorthEast | Front | G1 | [7 empty] | 8 |  | 38
East |  | G1
SouthEast | Left | G1 |  |  |  | 3 | [6 empty] | 16
South |  | G1
SouthWest | Back | G1 |  |  |  |  | 36 | 45 | [7 empty] | 15 |  | 15
West |  | G1
Sky Light |  | G1
Shaded |  | G1 | 6
Door 1 |  | D1 | 16.7 |  |  |  |  | 8
Door 2 |  | D2 | 17.8
Above Grade Walls |  |  | Above Grade Walls
Direction | Facing | Type | Entry | Family | PS WIC | PS Bath | PS Bed | Breakfast / Kitchen | Powder | Stairs | Loft | Master Bed | Master Bath | Master WIC | Bed 3 WIC | Bed 3 | Bath2 | Bed 4 | Hallway | Laundry | 0 | 0 | 0 | 0 | 0 | 0 | 0
NorthWest | Right | W1 | 99 | 94 |  |  |  | 138 | 48 | 130 | 85 | [6 empty] | 122
North |  | W1
NorthEast | Front | W1 | 84 | [6 empty] | 72 |  | 122
East |  | W1
SouthEast | Left | W1 |  |  | 50 | 78 | 138 |  |  |  |  | 138 | 60 | 62 | 29 | 94
South |  | W1
SouthWest | Back | W1 |  |  |  |  | 99 | 90 | [7 empty] | 94 | 42 | 73
West |  | W1
Exterior Perimeter |  |  | 25.5882 | 11.0588 | 5.8824 | 9.1765 | 27.8824 | 27.7647 | 5.6471 | 23.7647 | 10 | 30.5882 | 7.0588 | 7.2941 | 3.4118 | 22.1176 | 4.9412 | 22.9412 | - | - | - | - | - | - | - | - | -
Basement Walls
Direction | Facing | Type | Entry | Family | PS WIC | PS Bath | PS Bed | Breakfast / Kitchen | Powder | Stairs | Loft | Master Bed | Master Bath | Master WIC | Bed 3 WIC | Bed 3 | Bath2 | Bed 4 | Hallway | Laundry | 0 | 0 | 0 | 0 | 0 | 0 | 0
NorthWest | Right | W1
North |  | W1
NorthEast | Front | W1
East |  | W1
SouthEast | Left | W1
South |  | W1
SouthWest | Back | W1
West |  | W1
Exterior Perimeter |  |  | 4.0588 | - | - | - | - | 0.94118 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Other Walls | [27 empty] | O
Grade |  | W2
Partition |  | W1
Garage |  | W1 | 130 | 81 | 95
Attic |  | W3
Kneewall |  | W3
Roofs & Floors | [27 empty] | O
Ceiling |  | R1 | [7 empty] | 163 | 236 | 371 | 120 | 89 | 34 | 160 | 62 | 158 | 49 | 32 | [8 empty] | .
Vaulted |  | R2
Crawl/Uncon. |  | F1
Garage |  | F1 | [9 empty] | 371 | 28
Slab |  | F2 | 115 | 276 | 59 | 97 | 230 | 230 | 31

## Unit 1 a
Project |  |  | Carillon | [7 empty] | Date: | 2017-09-20 | [5 empty] | Typical Ceiling Height |  |  | 8.5
Location |  |  | Lawrenceville, GA | [7 empty] | By:
Description |  |  | Millhaven GL | [7 empty] | Level(s): | First Floor |  |  | Unit 1 a |  |  | Kneewall Height |  |  | 1
|  |  | Square Feet |  | 1474 | Volume | 13105 | Sf/Ton | 842.2857 |  | SEER | 14
[7 empty] | Ceiling Height |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 12 |  | 8.5 |  | 8.5 |  | 8.5 |  | 9 |  | 8.5 |  | 8.5 |  | 8 |  | 8 |  | 8
Components |  |  | CLTD (°F) | U-Value (Btu/hr-sf-°F) | Cooling Load Factor |  | Entire House |  | Stairs |  | Loft |  | Master Bed |  | Master Bath |  | Master WIC |  | Bed 3 WIC |  | Bed 3 |  | Bath2 |  | Bed 4 |  | Hallway |  | Laundry
| Type | Description |  |  |  |  | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr
Glass | G1 | NorthWest | Right | (E) | 18.3066 | Btu/hr-sf | 30 | 549.1995 |  | - | 30 | 549.1995 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | North |  | (SE) | 6.2013 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | NorthEast | Front | (S) | 7.8267 | Btu/hr-sf | 46 | 360.0286 | 8 | 62.6137 |  | - | 38 | 297.415 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | East |  | (SW) | 12.954 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | SouthEast | Left | (W) | 14.2712 | Btu/hr-sf | 16 | 228.3386 |  | - |  | - |  | - | 16 | 228.3386 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | South |  | (NW) | 15.8691 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | SouthWest | Back | (N) | 26.22 | Btu/hr-sf | 30 | 786.6 |  | - |  | - |  | - |  | - |  | - |  | - | 15 | 393.3 |  | - | 15 | 393.3 |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | West |  | (NE) | 29.1977 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | Sky Light |  |  | 40 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | Shaded |  |  | 6.2013 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Door | D1 | Door 1 | 21 | 0.5 | 10.5 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| D2 | Door 2 | 30 | 0.5 | 15 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Above Grade Walls | W1 | NorthWest | 19 | 0.077 | 1.463 | Btu/hr-sf | 337 | 493.031 | 130 | 190.19 | 85 | 124.355 |  | - |  | - |  | - |  | - |  | - |  | - | 122 | 178.486 |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | North | 13 | 0.077 | 1.001 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | NorthEast | 19 | 0.077 | 1.463 | Btu/hr-sf | 194 | 283.822 | 72 | 105.336 |  | - | 122 | 178.486 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | East | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthEast | 21 | 0.077 | 1.617 | Btu/hr-sf | 383 | 619.311 |  | - |  | - | 138 | 223.146 | 60 | 97.02 | 62 | 100.254 | 29 | 46.893 | 94 | 151.998 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | South | 16 | 0.077 | 1.232 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthWest | 21 | 0.077 | 1.617 | Btu/hr-sf | 209 | 337.953 |  | - |  | - |  | - |  | - |  | - |  | - | 94 | 151.998 | 42 | 67.914 | 73 | 118.041 |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | West | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Basement Walls | W1 | NorthWest | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | North | 13 | 0.077 | 1.001 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | NorthEast | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | East | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthEast | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | South | 16 | 0.077 | 1.232 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthWest | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | West | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Other | W2 | Grade | 0 | 0.067 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Partition | 10 | 0.077 | 0.77 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Garage | 30 | 0.077 | 2.31 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W3 | Attic | 55 | 0.053 | 2.915 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W3 | Kneewall | 55 | 0.053 | 2.915 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Roof | R1 | Ceiling | 55 | 0.026 | 1.43 | Btu/hr-sf | 1474 | 2107.82 | 163 | 233.09 | 236 | 337.48 | 371 | 530.53 | 120 | 171.6 | 89 | 127.27 | 34 | 48.62 | 160 | 228.8 | 62 | 88.66 | 158 | 225.94 | 49 | 70.07 | 32 | 45.76 |  | - |  | - |  | - |  | - |  | -
| R2 | Vaulted | 55 | 0.26 | 14.3 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Floor | F1 | Crawl/Uncon. | 11 | 0.053 | 0.583 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| F1 | Garage | 30 | 0.053 | 1.59 | Btu/hr-sf | 399 | 634.41 |  | - |  | - | 371 | 589.89 | 28 | 44.52 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| F2 | Slab | 0 | 0.1 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Internal |  | People |  |  | 255 | Btu/hr-sf | 4 | 1020 |  | - | 1 | 255 | 1 | 255 |  | - |  | - |  | - | 1 | 255 |  | - | 1 | 255 |  | - |  | - |  | - |  | - |  | - |  | - |  | -
|  | Lights |  |  | 3.413 | Btu/hr-sf | 199.5 | 682.6 |  | - |  | - | 185.5 | 634.818 | 14 | 47.782 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
|  | Appliances |  |  | 3.413 | Btu/hr-sf | 450 | 1535.85 |  | - | 250 | 853.25 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - | 200 | 682.6 |  | - |  | - |  | - |  | - |  | -
Volume | [5 empty] | CF | 13105 | 0 | 1385.5 | 0 | 2006 | 0 | 3153.5 | 0 | 1020 | 0 | 756.5 | 0 | 289 | 0 | 1920 | 0 | 527 | 0 | 1343 | 0 | 416.5 | 0 | 288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Infiltration (Tight) |  |  | 0.25 | ACH | 0.09 | Btu/hr-sf | 1474 | 1179.45 | 163 | 124.695 | 236 | 180.54 | 371 | 283.815 | 120 | 91.8 | 89 | 68.085 | 34 | 26.01 | 160 | 172.8 | 62 | 47.43 | 158 | 120.87 | 49 | 37.485 | 32 | 25.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Subtotal (Btu/hr) | [7 empty] | 10818.4137 |  | 715.9247 |  | 2299.8245 |  | 2993.1 |  | 681.0606 |  | 295.609 |  | 121.523 |  | 1353.896 |  | 204.004 |  | 1291.637 |  | 107.555 |  | 754.28 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
Safety Factor |  |  |  |  | 10% |  |  | 1081.8414 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Sensible Cooling Load (Btu/hr) | [7 empty] | 11900.2551 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Nominal Tons Required (75% sens. Cap.) | [7 empty] | 1.3223 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
System Selection |  |  | 1.75 | Tons | Space CFM |  |  | 700 |  | 46.3235 |  | 148.809 |  | 193.667 |  | 44.0677 |  | 19.1272 |  | 7.8631 |  | 87.6032 |  | 13.2 |  | 83.5747 |  | 6.9593 |  | 48.8053 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
Components |  |  | Detla T (°F) | U-Value (Btu/hr-sf-°F) | Heating Load Factor |  | Entire House |  | Stairs |  | Loft |  | Master Bed |  | Master Bath |  | Master WIC |  | Bed 3 WIC |  | Bed 3 |  | Bath2 |  | Bed 4 |  | Hallway |  | Laundry
| Type | Description |  |  |  |  | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr
Glass | G1 |  | 54 | 0.35 | 18.9 | Btu/hr-sf | 122 | 2305.8 | 8 | 151.2 |  | - | 38 | 718.2 | 16 | 302.4 |  | - |  | - | 15 | 283.5 |  | - | 15 | 283.5 |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G2 |  | 54 | 0 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G3 |  | 54 | 0 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Door | D1 |  | 54 | 0.5 | 27 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| D2 |  | 54 | 0.5 | 27 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Walls | W1 |  | 54 | 0.077 | 4.158 | Btu/hr-sf | 1123 | 4669.434 | 202 | 839.916 | 85 | 353.43 | 260 | 1081.08 | 60 | 249.48 | 62 | 257.796 | 29 | 120.582 | 188 | 781.704 | 42 | 174.636 | 195 | 810.81 |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W2 |  | 54 | 0.067 | 3.618 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W3 |  | 54 | 0.053 | 2.862 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Partition | 27 | 0.077 | 2.079 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W2 | Grade | 27 | 0.067 | 1.809 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Roof | R1 |  | 54 | 0.026 | 1.404 | Btu/hr-sf | 1474 | 2069.496 | 163 | 228.852 | 236 | 331.344 | 371 | 520.884 | 120 | 168.48 | 89 | 124.956 | 34 | 47.736 | 160 | 224.64 | 62 | 87.048 | 158 | 221.832 | 49 | 68.796 | 32 | 44.928 |  | - |  | - |  | - |  | - |  | -
| R2 |  | 54 | 0.26 | 14.04 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Floor | F1 |  | 54 | 0.053 | 2.862 | Btu/hr-sf | 399 | 1141.938 |  | - |  | - | 371 | 1061.802 | 28 | 80.136 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| F2 | Slab | 27 | 0.1 | 2.7 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Infiltration |  |  | 0.25 | ACH | 0.24 | Btu/hr-sf | 399 | 3145.2 | 0 | 332.52 | 0 | 481.44 | 371 | 756.84 | 28 | 244.8 | 0 | 181.56 | 0 | 69.36 | 0 | 460.8 | 0 | 126.48 | 0 | 322.32 | 0 | 99.96 | 0 | 69.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Subtotal | [7 empty] | 13331.868 |  | 1552.488 |  | 1166.214 |  | 4138.806 |  | 1045.296 |  | 564.312 |  | 237.678 |  | 1750.644 |  | 388.164 |  | 1638.462 |  | 168.756 |  | 114.048
Safety Factor |  |  |  |  | 15 | % |  | 1999.7802
Heat Loss |  |  | Nominal Size |  | 1.3449 | tons |  | 15331.6482
Minimum Heater Size | [7 empty] | 4.4921
System Selection |  |  | 5 | kW | Htg CFM |  |  | 700 |  | 81.5146 |  | 61.233 |  | 217.3112 |  | 54.8841 |  | 29.6296 |  | 12.4795 |  | 91.9189 |  | 20.3808 |  | 86.0287 |  | 8.8607 |  | 5.9882

## Unit 1 b
Project |  |  | Carillon | [7 empty] | Date: | 2017-09-20 | [5 empty] | Typical Ceiling Height |  |  | 8.5
Location |  |  | Lawrenceville, GA | [7 empty] | By:
Description |  |  | Millhaven GL | [7 empty] | Level(s): | First Floor |  |  | Unit 1 b |  |  | Kneewall Height |  |  | 1
|  |  | Square Feet |  | 1038 | Volume | 8823 | Sf/Ton | 593.1429 |  | SEER | 14
[7 empty] | Ceiling Height |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5
Components |  |  | CLTD (°F) | U-Value (Btu/hr-sf-°F) | Cooling Load Factor |  | Entire House |  | Entry |  | Family |  | PS WIC |  | PS Bath |  | PS Bed |  | Breakfast / Kitchen |  | Powder
| Type | Description |  |  |  |  | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr
Glass | G1 | NorthWest | Right | (E) | 18.3066 | Btu/hr-sf | 36 | 659.0394 |  | - | 36 | 659.0394 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | North |  | (SE) | 6.2013 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | NorthEast | Front | (S) | 7.8267 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | East |  | (SW) | 12.954 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | SouthEast | Left | (W) | 14.2712 | Btu/hr-sf | 3 | 42.8135 |  | - |  | - |  | - | 3 | 42.8135 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | South |  | (NW) | 15.8691 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | SouthWest | Back | (N) | 26.22 | Btu/hr-sf | 81 | 2123.82 |  | - |  | - |  | - |  | - | 36 | 943.92 | 45 | 1179.9 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | West |  | (NE) | 29.1977 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | Sky Light |  |  | 55 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | Shaded |  |  | 6.2013 | Btu/hr-sf | 6 | 37.2076 | 6 | 37.2076 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Door | D1 | Door 1 | 21 | 0.5 | 10.5 | Btu/hr-sf | 24.7 | 259.35 | 16.7 | 175.35 |  | - |  | - |  | - |  | - | 8 | 84 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| D2 | Door 2 | 30 | 0.5 | 15 | Btu/hr-sf | 17.8 | 267 | 17.8 | 267 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Above Grade Walls | W1 | NorthWest | 19 | 0.077 | 1.463 | Btu/hr-sf | 379 | 554.477 | 99 | 144.837 | 94 | 137.522 |  | - |  | - |  | - | 138 | 201.894 | 48 | 70.224 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | North | 13 | 0.077 | 1.001 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | NorthEast | 19 | 0.077 | 1.463 | Btu/hr-sf | 84 | 122.892 | 84 | 122.892 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | East | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthEast | 21 | 0.077 | 1.617 | Btu/hr-sf | 266 | 430.122 |  | - |  | - | 50 | 80.85 | 78 | 126.126 | 138 | 223.146 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | South | 16 | 0.077 | 1.232 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthWest | 21 | 0.077 | 1.617 | Btu/hr-sf | 189 | 305.613 |  | - |  | - |  | - |  | - | 99 | 160.083 | 90 | 145.53 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | West | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Basement Walls | W1 | NorthWest | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | North | 13 | 0.077 | 1.001 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | NorthEast | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | East | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthEast | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | South | 16 | 0.077 | 1.232 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthWest | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | West | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Other | W2 | Grade | 0 | 0.067 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Partition | 10 | 0.077 | 0.77 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Garage | 30 | 0.077 | 2.31 | Btu/hr-sf | 306 | 706.86 | 130 | 300.3 | 81 | 187.11 | 95 | 219.45 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W3 | Attic | 55 | 0.053 | 2.915 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W3 | Kneewall | 55 | 0.053 | 2.915 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Roof | R1 | Ceiling | 55 | 0.026 | 1.43 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| R2 | Vaulted | 55 | 0.26 | 14.3 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Floor | F1 | Crawl/Uncon. | 11 | 0.053 | 0.583 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| F1 | Garage | 30 | 0.053 | 1.59 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| F2 | Slab | 0 | 0.1 | 0 | Btu/hr-sf | 1038 | 0 | 115 | 0 | 276 | 0 | 59 | 0 | 97 | 0 | 230 | 0 | 230 | 0 | 31 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Internal |  | People |  |  | 255 | Btu/hr-sf | 2 | 510 |  | - | 1 | 255 |  | - |  | - | 1 | 255 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
|  | Lights |  |  | 3.413 | Btu/hr-sf | 521 | 1778.173 | 57.5 | 197.954 | 138 | 470.994 | 29.5 | 102.39 | 48.5 | 167.237 | 115 | 392.495 | 115 | 392.495 | 15.5 | 54.608 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
|  | Appliances |  |  | 3.413 | Btu/hr-sf | 930 | 3174.09 |  | - | 250 | 853.25 |  | - |  | - |  | - | 680 | 2320.84 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Volume | [5 empty] | CF | 8823 | 0 | 977.5 | 0 | 2346 | 0 | 501.5 | 0 | 824.5 | 0 | 1955 | 0 | 1955 | 0 | 263.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Infiltration (Tight) |  |  | 0.25 | ACH | 0.09 | Btu/hr-sf | 1038 | 794.07 | 115 | 87.975 | 276 | 211.14 | 59 | 45.135 | 97 | 74.205 | 230 | 175.95 | 230 | 175.95 | 31 | 23.715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Subtotal (Btu/hr) | [7 empty] | 11765.5275 |  | 1333.5156 |  | 2774.0554 |  | 447.825 |  | 410.3815 |  | 2150.594 |  | 4500.609 |  | 148.547 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
Safety Factor |  |  |  |  | 10% |  |  | 1176.5527 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Sensible Cooling Load (Btu/hr) | [7 empty] | 12942.0802 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Nominal Tons Required (75% sens. Cap.) | [7 empty] | 1.438 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
System Selection |  |  | 1.75 | Tons | Space CFM |  |  | 700 |  | 79.3386 |  | 165.0448 |  | 26.6437 |  | 24.416 |  | 127.9514 |  | 267.7675 |  | 8.8379 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
Components |  |  | Detla T (°F) | U-Value (Btu/hr-sf-°F) | Heating Load Factor |  | Entire House |  | Entry |  | Family |  | PS WIC |  | PS Bath |  | PS Bed |  | Breakfast / Kitchen |  | Powder
| Type | Description |  |  |  |  | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr
Glass | G1 |  | 54 | 0.35 | 18.9 | Btu/hr-sf | 126 | 2381.4 | 6 | 113.4 |  | - |  | - | 3 | 56.7 | 36 | 680.4 | 45 | 850.5 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G2 |  | 54 | 0 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G3 |  | 54 | 0 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Door | D1 |  | 54 | 0.5 | 27 | Btu/hr-sf | 24.7 | 666.9 | 16.7 | 450.9 |  | - |  | - |  | - |  | - | 8 | 216 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| D2 |  | 54 | 0.5 | 27 | Btu/hr-sf | 17.8 | 480.6 | 17.8 | 480.6 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Walls | W1 |  | 54 | 0.077 | 4.158 | Btu/hr-sf | 918 | 3817.044 | 183 | 760.914 | 94 | 390.852 | 50 | 207.9 | 78 | 324.324 | 237 | 985.446 | 228 | 948.024 | 48 | 199.584 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W2 |  | 54 | 0.067 | 3.618 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W3 |  | 54 | 0.053 | 2.862 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Partition | 27 | 0.077 | 2.079 | Btu/hr-sf | 306 | 636.174 | 130 | 270.27 | 81 | 168.399 | 95 | 197.505 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W2 | Grade | 27 | 0.067 | 1.809 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Roof | R1 |  | 54 | 0.026 | 1.404 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| R2 |  | 54 | 0.26 | 14.04 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Floor | F1 |  | 54 | 0.053 | 2.862 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| F2 | Slab | 27 | 0.1 | 2.7 | Btu/hr-sf | 1038 | 2802.6 | 115 | 310.5 | 276 | 745.2 | 59 | 159.3 | 97 | 261.9 | 230 | 621 | 230 | 621 | 31 | 83.7 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Infiltration |  |  | 0.25 | ACH | 0.24 | Btu/hr-sf | 1038 | 2117.52 | 115 | 234.6 | 276 | 563.04 | 59 | 120.36 | 97 | 197.88 | 230 | 469.2 | 230 | 469.2 | 31 | 63.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Subtotal | [7 empty] | 12902.238 |  | 2621.184 |  | 1867.491 |  | 685.065 |  | 840.804 |  | 2756.046 |  | 3104.724 |  | 346.524
Safety Factor |  |  |  |  | 15 | % |  | 1935.3357
Heat Loss |  |  | Nominal Size |  | 1.3015 | tons |  | 14837.5737
Minimum Heater Size | [7 empty] | 4.3474
System Selection |  |  | 5 | kW | Htg CFM |  |  | 700 |  | 142.2101 |  | 101.3191 |  | 37.1676 |  | 45.6171 |  | 149.5269 |  | 168.4442 |  | 18.8004

## Unit 2 a
Project |  |  | Carillon | [7 empty] | Date: | 2017-09-20 | [5 empty] | Typical Ceiling Height |  |  | 8.5
Location |  |  | Lawrenceville, GA | [7 empty] | By:
Description |  |  | Millhaven GL | [7 empty] | Level(s): | First Floor |  |  | Unit 2 a |  |  | Kneewall Height |  |  | 1
|  |  | Square Feet |  | 0 | Volume | 0 | Sf/Ton | 0 |  | SEER | 14
[7 empty] | Ceiling Height |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5
Components |  |  | CLTD (°F) | U-Value (Btu/hr-sf-°F) | Cooling Load Factor |  | Entire House
| Type | Description |  |  |  |  | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr
Glass | G1 | NorthWest | Right | (E) | 18.3066 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | North |  | (SE) | 6.2013 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | NorthEast | Front | (S) | 7.8267 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | East |  | (SW) | 12.954 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | SouthEast | Left | (W) | 14.2712 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | South |  | (NW) | 15.8691 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | SouthWest | Back | (N) | 26.22 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | West |  | (NE) | 29.1977 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | Sky Light |  |  | 55 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | Shaded |  |  | 6.2013 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Door | D1 | Door 1 | 21 | 0.5 | 10.5 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| D2 | Door 2 | 30 | 0.5 | 15 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Above Grade Walls | W1 | NorthWest | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | North | 13 | 0.077 | 1.001 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | NorthEast | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | East | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthEast | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | South | 16 | 0.077 | 1.232 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthWest | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | West | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Basement Walls | W1 | NorthWest | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | North | 13 | 0.077 | 1.001 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | NorthEast | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | East | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthEast | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | South | 16 | 0.077 | 1.232 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthWest | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | West | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Other | W2 | Grade | 0 | 0.067 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Partition | 10 | 0.077 | 0.77 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Garage | 30 | 0.077 | 2.31 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W3 | Attic | 55 | 0.053 | 2.915 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W3 | Kneewall | 55 | 0.053 | 2.915 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Roof | R1 | Ceiling | 55 | 0.026 | 1.43 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| R2 | Vaulted | 55 | 0.26 | 14.3 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Floor | F1 | Crawl/Uncon. | 11 | 0.053 | 0.583 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| F1 | Garage | 30 | 0.053 | 1.59 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| F2 | Slab | 0 | 0.1 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Internal |  | People |  |  | 255 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
|  | Lights |  |  | 3.413 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
|  | Appliances |  |  | 3.413 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Volume | [5 empty] | CF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Infiltration (Tight) |  |  | 0.25 | ACH | 0.09 | Btu/hr-sf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Subtotal (Btu/hr) | [7 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
Safety Factor |  |  |  |  | 10% |  |  | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Sensible Cooling Load (Btu/hr) | [7 empty] | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Nominal Tons Required (75% sens. Cap.) | [7 empty] | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
System Selection |  |  | 1.5 | Tons | Space CFM |  |  | 600 |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0!
Components |  |  | Detla T (°F) | U-Value (Btu/hr-sf-°F) | Heating Load Factor |  | Entire House
| Type | Description |  |  |  |  | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr
Glass | G1 |  | 54 | 0.35 | 18.9 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G2 |  | 54 | 0 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G3 |  | 54 | 0 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Door | D1 |  | 54 | 0.5 | 27 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| D2 |  | 54 | 0.5 | 27 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Walls | W1 |  | 54 | 0.077 | 4.158 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W2 |  | 54 | 0.067 | 3.618 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W3 |  | 54 | 0.053 | 2.862 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Partition | 27 | 0.077 | 2.079 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W2 | Grade | 27 | 0.067 | 1.809 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Roof | R1 |  | 54 | 0.026 | 1.404 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| R2 |  | 54 | 0.26 | 14.04 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Floor | F1 |  | 54 | 0.053 | 2.862 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| F2 | Slab | 27 | 0.1 | 2.7 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Infiltration |  |  | 0.25 | ACH | 0.24 | Btu/hr-sf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Subtotal | [7 empty] | 0
Safety Factor |  |  |  |  | 15 | % |  | 0
Heat Loss |  |  | Nominal Size |  | 0 | tons |  | 0
Minimum Heater Size | [7 empty] | 0
System Selection |  |  | 5 | kW | Htg CFM |  |  | 600

## Unit 2 b
Project |  |  | Carillon | [7 empty] | Date: | 2017-09-20 | [5 empty] | Typical Ceiling Height |  |  | 8.5
Location |  |  | Lawrenceville, GA | [7 empty] | By:
Description |  |  | Millhaven GL | [7 empty] | Level(s): | First Floor |  |  | Unit 2 b |  |  | Kneewall Height |  |  | 1
|  |  | Square Feet |  | 0 | Volume | 0 | Sf/Ton | 0 |  | SEER | 14
[7 empty] | Ceiling Height |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5
Components |  |  | CLTD (°F) | U-Value (Btu/hr-sf-°F) | Cooling Load Factor |  | Entire House
| Type | Description |  |  |  |  | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr
Glass | G1 | NorthWest | Right | (E) | 18.3066 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | North |  | (SE) | 6.2013 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | NorthEast | Front | (S) | 7.8267 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | East |  | (SW) | 12.954 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | SouthEast | Left | (W) | 14.2712 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | South |  | (NW) | 15.8691 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | SouthWest | Back | (N) | 26.22 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | West |  | (NE) | 29.1977 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | Sky Light |  |  | 55 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | Shaded |  |  | 6.2013 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Door | D1 | Door 1 | 21 | 0.5 | 10.5 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| D2 | Door 2 | 30 | 0.5 | 15 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Above Grade Walls | W1 | NorthWest | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | North | 13 | 0.077 | 1.001 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | NorthEast | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | East | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthEast | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | South | 16 | 0.077 | 1.232 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthWest | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | West | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Basement Walls | W1 | NorthWest | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | North | 13 | 0.077 | 1.001 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | NorthEast | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | East | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthEast | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | South | 16 | 0.077 | 1.232 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthWest | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | West | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Other | W2 | Grade | 0 | 0.067 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Partition | 10 | 0.077 | 0.77 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Garage | 30 | 0.077 | 2.31 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W3 | Attic | 55 | 0.053 | 2.915 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W3 | Kneewall | 55 | 0.053 | 2.915 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Roof | R1 | Ceiling | 55 | 0.026 | 1.43 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| R2 | Vaulted | 55 | 0.26 | 14.3 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Floor | F1 | Crawl/Uncon. | 11 | 0.053 | 0.583 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| F1 | Garage | 30 | 0.053 | 1.59 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| F2 | Slab | 0 | 0.1 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Internal |  | People |  |  | 255 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
|  | Lights |  |  | 3.413 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
|  | Appliances |  |  | 3.413 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Volume | [5 empty] | CF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Infiltration (Tight) |  |  | 0.25 | ACH | 0.09 | Btu/hr-sf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Subtotal (Btu/hr) | [7 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
Safety Factor |  |  |  |  | 10% |  |  | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Sensible Cooling Load (Btu/hr) | [7 empty] | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Nominal Tons Required (75% sens. Cap.) | [7 empty] | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
System Selection |  |  | 1.5 | Tons | Space CFM |  |  | 600 |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0!
Components |  |  | Detla T (°F) | U-Value (Btu/hr-sf-°F) | Heating Load Factor |  | Entire House
| Type | Description |  |  |  |  | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr
Glass | G1 |  | 54 | 0.35 | 18.9 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G2 |  | 54 | 0 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G3 |  | 54 | 0 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Door | D1 |  | 54 | 0.5 | 27 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| D2 |  | 54 | 0.5 | 27 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Walls | W1 |  | 54 | 0.077 | 4.158 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W2 |  | 54 | 0.067 | 3.618 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W3 |  | 54 | 0.053 | 2.862 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Partition | 27 | 0.077 | 2.079 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W2 | Grade | 27 | 0.067 | 1.809 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Roof | R1 |  | 54 | 0.026 | 1.404 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| R2 |  | 54 | 0.26 | 14.04 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Floor | F1 |  | 54 | 0.053 | 2.862 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| F2 | Slab | 27 | 0.1 | 2.7 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Infiltration |  |  | 0.25 | ACH | 0.24 | Btu/hr-sf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Subtotal | [7 empty] | 0
Safety Factor |  |  |  |  | 15 | % |  | 0
Heat Loss |  |  | Nominal Size |  | 0 | tons |  | 0
Minimum Heater Size | [7 empty] | 0
System Selection |  |  | 5 | kW | Htg CFM |  |  | 600

## Unit 3 a
Project |  |  | Carillon | [7 empty] | Date: | 2017-09-20 | [5 empty] | Typical Ceiling Height |  |  | 8.5
Location |  |  | Lawrenceville, GA | [7 empty] | By:
Description |  |  | Millhaven GL | [7 empty] | Level(s): | First Floor |  |  | Unit 3 a |  |  | Kneewall Height |  |  | 1
|  |  | Square Feet |  | 0 | Volume | 0 | Sf/Ton | 0 |  | SEER | 14
[7 empty] | Ceiling Height |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5
Components |  |  | CLTD (°F) | U-Value (Btu/hr-sf-°F) | Cooling Load Factor |  | Entire House
| Type | Description |  |  |  |  | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr
Glass | G1 | NorthWest | Right | (E) | 18.3066 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | North |  | (SE) | 6.2013 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | NorthEast | Front | (S) | 7.8267 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | East |  | (SW) | 12.954 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | SouthEast | Left | (W) | 14.2712 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | South |  | (NW) | 15.8691 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | SouthWest | Back | (N) | 26.22 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | West |  | (NE) | 29.1977 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | Sky Light |  |  | 55 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G1 | Shaded |  |  | 6.2013 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Door | D1 | Door 1 | 21 | 0.5 | 10.5 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| D2 | Door 2 | 30 | 0.5 | 15 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Above Grade Walls | W1 | NorthWest | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | North | 13 | 0.077 | 1.001 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | NorthEast | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | East | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthEast | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | South | 16 | 0.077 | 1.232 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthWest | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | West | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Basement Walls | W1 | NorthWest | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | North | 13 | 0.077 | 1.001 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | NorthEast | 19 | 0.077 | 1.463 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | East | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthEast | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | South | 16 | 0.077 | 1.232 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | SouthWest | 21 | 0.077 | 1.617 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | West | 23 | 0.077 | 1.771 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Other | W2 | Grade | 0 | 0.067 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Partition | 10 | 0.077 | 0.77 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Garage | 30 | 0.077 | 2.31 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W3 | Attic | 55 | 0.053 | 2.915 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W3 | Kneewall | 55 | 0.053 | 2.915 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Roof | R1 | Ceiling | 55 | 0.026 | 1.43 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| R2 | Vaulted | 55 | 0.26 | 14.3 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Floor | F1 | Crawl/Uncon. | 11 | 0.053 | 0.583 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| F1 | Garage | 30 | 0.053 | 1.59 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| F2 | Slab | 0 | 0.1 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Internal |  | People |  |  | 255 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
|  | Lights |  |  | 3.413 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
|  | Appliances |  |  | 3.413 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Volume | [5 empty] | CF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Infiltration (Tight) |  |  | 0.25 | ACH | 0.09 | Btu/hr-sf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Subtotal (Btu/hr) | [7 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
Safety Factor |  |  |  |  | 10% |  |  | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Sensible Cooling Load (Btu/hr) | [7 empty] | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Nominal Tons Required (75% sens. Cap.) | [7 empty] | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
System Selection |  |  | 1.5 | Tons | Space CFM |  |  | 600 |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0!
Components |  |  | Detla T (°F) | U-Value (Btu/hr-sf-°F) | Heating Load Factor |  | Entire House
| Type | Description |  |  |  |  | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr | Qty | Btu/hr
Glass | G1 |  | 54 | 0.35 | 18.9 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G2 |  | 54 | 0 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| G3 |  | 54 | 0 | 0 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Door | D1 |  | 54 | 0.5 | 27 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| D2 |  | 54 | 0.5 | 27 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Walls | W1 |  | 54 | 0.077 | 4.158 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W2 |  | 54 | 0.067 | 3.618 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W3 |  | 54 | 0.053 | 2.862 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W1 | Partition | 27 | 0.077 | 2.079 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| W2 | Grade | 27 | 0.067 | 1.809 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Roof | R1 |  | 54 | 0.026 | 1.404 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| R2 |  | 54 | 0.26 | 14.04 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Floor | F1 |  | 54 | 0.053 | 2.862 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
| F2 | Slab | 27 | 0.1 | 2.7 | Btu/hr-sf | 0 | 0 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | -
Infiltration |  |  | 0.25 | ACH | 0.24 | Btu/hr-sf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Subtotal | [7 empty] | 0
Safety Factor |  |  |  |  | 15 | % |  | 0
Heat Loss |  |  | Nominal Size |  | 0 | tons |  | 0
Minimum Heater Size | [7 empty] | 0
System Selection |  |  | 5 | kW | Htg CFM |  |  | 600

## Glass CLF Calculation
[7 empty] | 2022 | 2019 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2021 | 2022 | 2022 | 2022 | 2020 | 2022 | 2018 | 2017 | 2017 | 2021 | 2020 | 2021 | 2017 | 2019 | 2019 | 2022 | 2023 | 2020
[7 empty] | Hoschton | Hoschton | Jefferson | Oakwood | Oakwood | Oakwood | Oakwood | Oakwood | Gainesville | Jefferson | Jefferson | Jefferson | Jefferson | Jefferson | Jefferson | Hoschton | Homer | Homer | Homer | Buford | Buford | Statham | Statham | Bethlehem | Dacula | Dacula
Window | TableGLF | Corrected | Applied GLF | Mystery CF |  | CLF | Sidney | Chelsea | 2831 | Sally - A Slab | Hawthorn II - Slab |  | Pembrooke | Chestnut | Chadwick | Reed | 1755 | 1921 | R-7 | Nassick | Devon Gales | Abbeyville | Englemoore | Nelson | Nicklaus | Dakota D | Sienna | Ellijay | Finley | Bradley | Ruth Ann | Monroe
NorthWest | 59 |  | 59 | 0.56 | 0.1232 | 18.3066 | 17 | 22 | 25 | 21 | 21 | 21 | 21 | 21 | 18 | 17 | 25 | 25 | 18 | 17 | 23 | 21.68 | 21 | 23 | 23 | 18 | 18 | 21 | 21 | 21 | 18 | 21
North | 34 |  | 34 | 0.1765 | 0.03883 | 6.2013 | 6 | 7 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 6 | 6 | 6 | 7 | 6 | 7 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 6
NorthEast | 59 |  | 59 | 0.156 | 0.03432 | 7.8267 | 7 | 9 | 9 | 8 | 8 | 8 | 8 | 8 | 7 | 9 | 9 | 9 | 7 | 7 | 9 | 8.69 | 8 | 9 | 9 | 8 | 8 | 8 | 8 | 8 | 8 | 8
East | 81 |  | 81 | 0.25 | 0.055 | 12.954 | 12 | 16 | 17 | 15 | 15 | 15 | 15 | 15 | 12 | 12 | 17 | 17 | 13 | 12 | 16 | 15 | 15 | 16 | 16 | 13 | 13 | 15 | 15 | 15 | 13 | 15
SouthEast | 73 |  | 73 | 0.32 | 0.0704 | 14.2712 | 13 | 17 | 19 | 16 | 16 | 16 | 16 | 16 | 14 | 13 | 19 | 19 | 14 | 13 | 17 | 16.66 | 16 | 18 | 18 | 14 | 14 | 16 | 16 | 16 | 14 | 16
South | 81 | 63.18 | 63.18 | 0.432 | 0.09504 | 15.8691 | 14 | 19 | 21 | 18 | 18 | 18 | 18 | 18 | 15 | 15 | 21 | 21 | 15 | 15 | 19 | 18 | 18 | 20 | 20 | 16 | 16 | 18 | 18 | 18 | 16 | 18
SouthWest | 73 | 56.94 | 56.94 | 0.9 | 0.198 | 26.22 | 24 | 32 | 37 | 31 | 31 | 31 | 31 | 31 | 26 | 25 | 37 | 37 | 26 | 25 | 34 | 31.22 | 31 | 34 | 34 | 26 | 26 | 31 | 31 | 31 | 26 | 31
West | 50 |  | 50 | 1.18 | 0.2596 | 29.1977 | 27 | 36 | 42 | 35 | 35 | 35 | 35 | 35 | 29 | 28 | 42 | 42 | 29 | 28 | 38 | 35 | 35 | 39 | 39 | 29 | 29 | 35 | 35 | 35 | 29 | 35
|  |  |  | U |  | 0.35 | 0.32 | 0.35 | 0.31 | [8 empty] | 0.31 | 0.31 | 0.3 | 0.3 | 0.35 | 0.33 | 0.33 | 0.33 | 0.35 | 0.35 | 0.33
|  |  |  | SHGC |  | 0.22 | 0.2 | 0.28 | 0.33 | [8 empty] | 0.33 | 0.22 | 0.21 | 0.3 | 0.27 | 0.27 | 0.3 | 0.3 | 0.22 | 0.22 | 0.27
|  |  |  | GLF correction |  | -0.22 | [5 empty] | CLTD | U | SHGC
Door
D1 | [5 empty] | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
D2 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Wall
NorthWest | [5 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
North | [5 empty] | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
NorthEast | [5 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
East | [5 empty] | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23
SouthEast | [5 empty] | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
South | [5 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
SouthWest | [5 empty] | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
West | [5 empty] | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23
Attic Insulation Types
R-30 Blown
R-30 Batt | [11 empty] | SCa | SCt | GLFt | Ut | Ua | Dt | DR | To | Ta
R-38 Blown | [11 empty] | 0.5 | 0.45 | 81 | 0.55 | 0.35 | 10.8 | 18.4 | 95 | 85.8
R-45 Blown
R-49 Blown
R-50 Blown | [11 empty] | 87.18 | 0
R-21 Spray Foam
Unit 1 a
Unit 1 b
Unit 2 a
Unit 2 b
Unit 3 a
Unit 3 b
Unit 4
Unit 5